## Audit Register
Punjab & Sind Bank – Integrated e-Surveillance Audit – Site Audit Register
Sr. No. | Date of Audit | ATM / CRM ID | Branch Name | Location / Address | City | Zone / Zonal Office | Region / FGMO | Audit Team – Lead Auditor | Audit Team – Members | Vendor Representative (Name / Contact) | Bank Official Present (Name / Designation) | Audit Start Time | Audit End Time | Hardware – Result | Functional – Result | Network & Cyber – Result | Overall Result | No. of Observations | Report Ref. No. | Report Date | Remarks
1 | 2026-09-14 | PSB-DEL-0142 | Rajouri Garden | Shop 12, Main Market, Rajouri Garden | New Delhi | ZO Delhi | FGMO North | A. Sharma | R. Verma; S. Kaur | Vendor site engineer – 98xxxxxxxx | Branch Manager – Mr. X | 10:30 | 13:15 | Compliant | Partially Compliant | Compliant | Partially Compliant | 3 | IFIT/PSB/ES/2026-27/001 | 2026-09-16 | NVR retention short of 180 days; re-verification due 30-09-2026
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
Row 5 is an example entry – overwrite it with actual data.

## Checklist
Punjab & Sind Bank - Integrated e-Surveillance System at ATMs/CRMs |  |  | INFOCUS-IT (CERT-In empanelled IS auditor)
| Site / ATM ID and location: |  |  | Audit date:
| Auditor(s) / team: |  |  | Zone / FGMO:
| Vendor representative: |  |  | Bank official:
ID | Checkpoint |  | How to verify | Status | Remarks / Observation
A. HARDWARE VERIFICATION
HW-01 | Installed equipment matches the approved site list / BoM - make, model, serial no. and quantity |  | Physical count vs BoM
HW-02 | CCTV cameras cover ATM room, back room / UPS cabinet, front lobby and front entrance |  | Site walk-through; live feed
HW-03 | Cameras support H.265 (or better) compression; edge analytics (motion / tamper / intrusion) where offered |  | Datasheet; camera config page
HW-04 | No camera or sensor is positioned to capture customer credentials (PIN pad / screen) |  | Check field of view of each camera
HW-05 | NVR placed in back room, physically secured, storage sized for minimum 180 days recording |  | Inspect NVR; storage calculation
HW-06 | Sensors installed and healthy - thermal, removal detector, vibration, tilt, motion (PIR), smoke |  | Physical check; panel status
HW-07 | Intruder alarm system / control panel and fire detection (abnormal heat / smoke) installed; panel tamper protected |  | Physical check
HW-08 | Two-way audio unit (speaker and microphone) installed and audible |  | Physical check; test call
HW-10 | OEMs of cameras, NVR, switches and accessories not restricted / blacklisted by Govt. of India; BIS certification held for applicable models |  | OEM declaration; BIS certificates
HW-11 | Site preparation, mounting and cabling done safely; old e-surveillance equipment de-installed |  | Visual inspection
B. FUNCTIONAL & QUALITY TESTING
FT-01 | Intrusion / unauthorised activity (PIR / IP camera) raises a real-time alert at CMS, 24x7, including ATMs closed at night; operator verifies by video |  | Simulate event; observe CMS
FT-02 | Each sensor (thermal, removal, vibration, tilt, motion, smoke) triggers the correct alert with site and sensor ID |  | Trigger each sensor
FT-03 | Camera analytics detects covered face / mask / helmet and loitering, and auto-generates an alert ticket |  | Test with mask / helmet
FT-04 | Two-way audio is clear and stays available on link loss; pre-recorded deterrent message of at least 60 seconds plays |  | Audio test; link-down test
FT-05 | Recording retained 180 days or more at site NVR and 7-day backup at CMS; flagged cases retained till closure |  | Check oldest recording available
FT-06 | Video quality and FPS fit for forensic / legal use; date-time stamp correct |  | Playback review
FT-07 | On-demand audio / video pull from CMS; footage given to Bank within 24 hours; export on portable device for police |  | Sample footage request
FT-08 | Alerts sent by SMS / email / call to Branch, Zone and HO officials per escalation matrix; telephone escalation to police etc. |  | Test alert; escalation log
FT-09 | Tickets auto-created and tracked till closure; ticket notes and call recordings kept 180 days or more |  | Sample tickets
FT-10 | Bank can remotely view any ATM and run mock drills (logs available); CMS can remotely control site devices |  | Mock drill; demo from CMS
FT-11 | Automated health checks - camera, HDD, sensor, video housekeeping - with status reports at set intervals |  | Health reports
FT-12 | Web portal and mobile app - real-time status, UP/DOWN with equipment-wise downtime age, live view, screenshots, manual ticket, incident history; role-wise access for BM / ZM / FGMO / ATM Cell / HO Security |  | Portal and app walk-through
FT-13 | Required reports available - uptime, incident, system down, health, ATM-wise alerts, tickets, power cut, chest door / hood open, link uptime, PM, site audit |  | Generate sample reports
FT-15 | 24x7 live screen (LCD) at HO Security Department shows parallel feed of alerts, CCTV status and sensor / equipment health |  | Observe at HO
FT-16 | Preventive maintenance done per quarterly schedule; faults rectified within 24 hrs (metro / urban) or 48 hrs (others); standby equipment and spares available; signed PM and monthly health reports |  | PM reports; fault tickets; spares register
C. NETWORK & CYBER SECURITY
NS-01 | Site-to-CMS connectivity runs over a secure, dedicated VPN (GSM / CDMA) |  | Network diagram; VPN config
NS-02 | Redundant connectivity from two different service providers; failover works; link uptime reported |  | Pull primary link; uptime report
NS-03 | Minimum AES-256 encryption for all video feeds and data at rest |  | Config review; traffic capture
NS-04 | Default credentials disabled on cameras, NVR, panels, routers and CMS |  | Login test with default passwords
NS-05 | Role-based access control (RBAC) on CMS, portal and mobile app; user list reviewed |  | User-role matrix
NS-06 | Multi-factor authentication (MFA) for all administrative access |  | Admin login test
NS-07 | Audit logs of all administrative actions and audit trail of all access / actions retained and protected |  | Sample log review
NS-08 | Security hardening of all hardware and software - unused ports / services closed, firmware and patches current |  | Port scan; firmware versions
NS-09 | All video, metadata and analytics data stays in India (no transfer abroad without Bank's written approval); cloud / hybrid hosting complies with RBI data localisation and DPDP Act, 2023 |  | Hosting details; data-flow; declaration
NS-10 | Annual security audit and VAPT (infrastructure, portal, mobile app) by CERT-In empanelled auditor; compliance certificate submitted to Bank; findings closed |  | VAPT report; certificate; closure tracker
NS-11 | 7-day central backup is restorable and encrypted |  | Restore test
NS-12 | CMS integration with Bank's Incident Response System, ATM monitoring, ticketing tools and SOC is working, secure and compliant with Bank's IT guidelines |  | Integration test; SOC logs
| Lead auditor - name, signature, date: |  |  | Bank official:
| Vendor representative - name, signature, date: |  |  | Date:
| Section | Total checks | Compliant | Partial | Non-Compliant | NA | Pending | % Compliant (of applicable)
| A. HARDWARE VERIFICATION | 10 | 0 | 0 | 0 | 0 | 10 | 0%
| B. FUNCTIONAL & QUALITY TESTING | 15 | 0 | 0 | 0 | 0 | 15 | 0%
| C. NETWORK & CYBER SECURITY | 12 | 0 | 0 | 0 | 0 | 12 | 0%
| TOTAL | 37 | 0 | 0 | 0 | 0 | 37 | 0%